## Slide 1
Position, type, length of the thermocouples
Project- Extension

## Slide 2
A0. Design of the measuring pipe
1. 3 pipes connected in series, 4,5 m each, 4 VIP panels-length as measuring area
2. Two thicknesses of VIP will be used: 6 and 8 mm, and panels has Al foil in both sides
3. 300 mm ordinary pipe can be reduced to 200 mm
4. Dimension of the VIPs: 6mm thick, 970 mm length, 294 width
5. Dimension of the VIPs: 8mm thick, 970 mm length, XXX width
Part A
General dimensions:4600mm (measuring area)
VIP
Ordinary pipe
Ordinary pipe
300
1000
1000
1000
VIP
VIP
VIP
300
1000
4600 mm

## Slide 3
Section 2
TCX 4
TCX 7
TCX 6
Section 1
TCX 1
Section 3
TCX 5
Section 4
TCX 2
Pipe 1
Position of TCs: in the middle of sections
VIP-6mm
Ordinary pipe
Ordinary pipe
300
1000
1000
1000
300
1000
4600 mm
VIP-6mm
VIP-6mm
VIP-6mm
length
TCX1, TCX2, TX3 (Supply temperature) 2 meters (80 cm out of measuring area)
TCX4, TCX5, TCX6, TX7 (3 VIP, 1 PEX, 1 mantel) 3 meters (180 cm out of measuring area)
Section 1
Section 2
Section 3
Section 4
The aim is to determine the influence of Al-foil on both sides.
TCX 3
Total 7 TC
Section 1: should be damaged

## Slide 4
Section 2
TCX 11
TCX 14
TCX 13
Section 1
TCX 8
Section 3
TCX 12
Section 4
TCX 9
Pipe 2
Position of TCs: in the middle of sections
VIP-8mm
Ordinary pipe
Ordinary pipe
300
1000
1000
1000
300
1000
4600 mm
VIP-8mm
VIP-8mm
VIP-8mm
length
TCX8, TCX9, TCX10 (Supply temperature) 2 meters (80 cm out of measuring area)
TCX11, TCX12, TCX13, TCX14 (3 VIP, 1 PEX, 1 mantel) 3 meters (180 cm out of measuring area)
Section 1
Section 2
Section 3
Section 4
The aim is to determine the influence of VIP thickness.
Section 1: should be damaged
Total 7 TC
TCX 10

## Slide 5
Section 2
TCX 19,20
TCX 26
TCX 25
Section 1
TCX 15
Section 3
TCX 21,22
Section 4
TCX 16
Pipe 3
2layers of VIP
Position of TCs: in the middle of sections
length
TCX15 toTCX18, TCX23, TCX24 (2Supply temperature, 4 VIP)2 meters (80 cm out of measuring area)
TCX19 to TCX22, TCX25, TCX26 (4 VIP, 1 PEX, 1 mantel) 3 meters (180 cm out of measuring area)
VIP-8/6mm
Ordinary pipe
Ordinary pipe
300
1000
1000
1000
300
1000
4600 mm
VIP-8/6mm
VIP-8/6mm
VIP-8/6mm
Section 1
Section 2
Section 3
Section 4
The aim is to determine the influence of VIP thickness.
TCX 17,18
TCX 23,24
Section 1: should be damaged
Total 12 TC

## Slide 6
Total number of TC: 26 st
Thermocouples and temperature measurements
length
TCX1, TCX2, TX3 (Supply temperature) 2 meters (80 cm out of measuring area)
TCX4, TCX5, TCX6, TX7 (3 VIP, 1 PEX, 1 mantel) 3 meters (180 cm out of measuring area)
length
TCX8, TCX9, TCX10 (Supply temperature) 2 meters (80 cm out of measuring area)
TCX11, TCX12, TCX13, TCX14 (3 VIP, 1 PEX, 1 mantel) 3 meters (180 cm out of measuring area)
length
TCX15 toTCX18, TCX23, TCX24 (2Supply temperature, 4 VIP)2 meters (80 cm out of measuring area)
TCX19 to TCX22, TCX25, TCX26 (4 VIP, 1 PEX, 1 mantel) 3 meters (180 cm out of measuring area)
12 TC of length 2 meter
14 TC of length 3 meter

## Slide 7
- Thermo-couples will draw out to the left and right sides of the pipes for connecting to the logger. We need at least 26 channels (13 in each logger).
Logger
Logger
Pipe 1
Pipe 2
Pipe 3
Heat source